# Summary

This document is designed to inform users about the usage of the 4Evac Manager application. This document is written for people that are familiar with 4Evac devices. The general workflow will be discussed first and afterwards the different application screens will be described. The last chapter shows the devices that can be configured with the 4Evac Manager application.

The application works on Windows 7 and up. Older versions and other platforms are not supported to date.

USER MANUAL

| Rev. | Date | Nature of Changes | Approved By |
| --- | --- | --- | --- |
| 22 | 17-03-2021 | Updated for 4Evac Manager Version 5.3G | TC |
| 23 | 30-11-2021 | Updated for 4Evac Manager Version 5.3K | TC |
| 24 | 30-06-2022 | Updated for 4Evac Manager Version 5.4 | TC |

www.4Evac.com

Table of Contents:

Summary	1

1. Modifying Configuration Files	3

1.1.	Data exchange by SD-Card	3

1.2.	Data exchange by Online Configuration	3

2. Application workflow	4

3. Application Usage	5

3.1. Device overview	5

3.2. Zone overview	48

3.3. Sources overview	52

3.4. Event overview	55

3.5. Evac Matrix	66

3.6. Live Monitoring	67

3.7. More Settings	72

3.7.1 Global Configuration Settings	72

3.7.2 Application Settings	72

3.7.3 Synchronize Time	73

3.8. Clear, Open, Save, Download and Upload configuration	74

4. Supported devices	76

# Modifying Configuration Files

There are 2 ways to update the configuration files. The first way is to extract the SD-Card and put a new configuration on it via pc. The second, is updating the configuration files via online configuration. Both options are described below.

## Data exchange by SD-Card

To update the configuration on the SD-Card, the card needs to be retrieved from a C500 and inserted in a computer. The configuration can be opened and edited with the 4Evac Manager Application. It is also possible to create a new configuration offline and save this to the SD-Card.

After updating the configuration on the SD-Card, it should be once again inserted in the SD-Card holder. To use the new configuration, the C500 needs to be rebooted. This can be done by holding down the ‘Function’ key and pressing the ‘Reset’ key on the front panel. Alternatively, the C500 can be rebooted by pressing the ‘Reset’ button on the mainboard.

Note: Be careful when extracting the SD-card from the C500. The SD-Card holder is fragile and requires delicate handling.

## Data exchange by Online Configuration

Existing configuration files can be retrieved and updated via the online configuration mode of this application. To use this mode, the application needs to be connected to the system via a serial port to a C500 local net port. The com port is selected in the ‘More’ tab and a connection is established by pressing the ‘Connect’ button.

Once the connection is established, the ‘Read’ and ‘Send’ buttons become available.

Pressing ‘Read’ starts the configuration file reading. This can prompt the user to select a device when more than 1 is found and the ‘Show Download Device Selection’ option is set accordingly. When a device is selected, the file download will begin and a progress bar shows the current status.

Pressing ‘Send starts the configuration file sending. It is required that a valid configuration is available and all configured global net devices are connected to the system. Once this is verified, the upload will start and a progress bar shows the current status.

# Application workflow

This chapter describes the general workflow that should be followed when creating a new configuration. Detailed information about each window can be found in the next chapter.

- Add the devices

  - (C500 device) Edit C500 devices to set the correct number of amplifiers, the available background music inputs and integrated fireman microphone usage

- Add the zones

- Add the messages (at least Evac type)

- Add the events

- Go back to edit the device settings for the created events and zones

  - Connect the created events and zones

  - Review and change the remaining device settings

- Review the zones and message types that are activated by the evacuation inputs

- Review and edit the additional settings.

- Save the configuration

# Application Usage

This chapter describes each application window in detail. These screens will be explained in the order they are found in the application.

## Device overview

The device overview contains the following important buttons:

- Add button: Opens a dialog to create a new device.

- Edit button: Opens a dialog to edit the selected device.

- Copy button: Duplicate the selected device. The name is automatically generated and the id is incremented.

- Delete button: Remove the selected device. (When Holding the Ctrl button, it gives the option to delete all devices)

Image 1 Devices Overview

### Add Device Dialog

This dialog is used to create a new device and has the following options:

- Select the device type.

- Select the device name. If this field is left empty, a name will be generated automatically.

- Select the device ID. (Default: the first available ID)

- Select the device priority. A lower number indicates a higher priority. (Default: 0)

Image 2 Add Device Dialog

### Edit Device Dialog C500

This dialog is used to edit a C500 device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Select if the backup amplifier is available. (Default: disabled)

- Select if the integrated fireman microphone is available. (Default: disabled)

- Select if the front panel key is used. (Default: disabled)

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The C500 device has the following six tabs with settings:

### Amplifier Tab:

- Select which speaker lines are enabled.

- Select if the amplifier is bridged.

- Select if the amplifier is monitored.

- Select if the speaker line EOL is monitored. Disable when line faults should not be reported or speaker line monitoring is taken over by another device.

- Select the monitoring tone level. (Default: -35 dB)

- Select the impedance tolerance. (Default: 50%)

- Select if a high level 20 kHz tone is activated during emergency audio types (All evacuation and alert types)

- Select if a high level 20 kHz tone is activated during paging audio types (All general types, except BGM)

- Select the high level 20 kHz tone level. (Default: -25 dB)

- Set the equalizer options. (See 3.1.14.1)

- Set the volume for the speaker line. (Default: -6 dB or 0dB, depending on the “Default Audio Level” setting)

- Select if a SW6 unit is connected to the amplifier.

Image 3 C500 Amplifier Tab

### BGM Tab:

- Select which audio inputs are enabled. The first channel is automatically enabled when the integrated fireman microphone checkbox is selected. The second channel can be used as a background music input.

- Select if the input is used for the live evacuation events, instead of background music.

- Set the equalizer options. (See 3.1.14.1)

- Set the volume for the audio input channel. (Default: -9 dB or 0dB, depending on the “Default Audio Level” setting)

Image 4 C500 Background Music Tab

### Evac Inputs Tab:

- Select if the input is monitored. When monitoring is disabled, faults will not be reported.

- Select if the input is normally open or normally closed. (Default: Normally Open)

- Select if the input is pulse triggered. When this option is enabled, the event will stay active until the device is reset. Otherwise, it will be set to level sensitive. (Default: Level sensitive)

- Select the input function. This makes it possible to use the input for different types of event activation. (Default: Event Activation (Level) (This is disabled for the silence and reset inputs)

- Select which events are activated by the input.

Image 5 C500 Evac Inputs Tab

### GPI Tab:

- Select if the input is normally open or normally closed. 2(Default: Normally Open)

- Select if the input is pulse triggered. When this option is enabled, the event will stay active until the device is reset. Otherwise, it will be set to level sensitive. (Default: Level sensitive)

- Select the input function. This makes it possible to use the input for different types of event activation. (Default: Event Activation (Level))

- Select which events are activated by the input.

Image 6 C500 Gpi Tab

### GPO Tab:

- Select when the output is activated. (Default: Active High)

  - Active High: The output is closed when a connected event is active.

  - Active Low: The output is closed when a connected event is inactive.

- Select what zone state and / or device fault activates the output. (See 3.1.14.2)

- Show the event names that trigger this output.

Image 7 C500 Gpo Tab

### Front Panel Tab:

- Select which zone is connected to each selection button. A zone can only be linked to 1 button at a time.

- When checking ‘Select First Available Zones’ it will connect the first 6 zones to the buttons.

Image 8 C500 Front Panel Tab

### Edit Device Dialog Impact

This dialog is used to edit an impact device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Select if the device uses a maze module and select the maze module id. (The maze module id should be selected to make the “Maze Available” setting to stay checked)

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The impact device has the following tabs with settings:

### Amplifier Tab

- Select the number of connected amplifiers.

- Select if the connected amplifiers are maze amplifiers. (When not selected all amplifiers are expected to be normal amplifiers) This setting can only be used when the controller is also using a maze module.

- In case of normal amplifiers select for each:

  - SW6 device connection to CHA (By clicking the Change… button)

  - SW6 device connection to CHB (By clicking the Change… button)

  - Amplifier channel B backup or normal usage

  - Charger Group: When multiple amplifiers have the same charger group, they should work together to charge 1 set of batteries.

- In case of maze amplifiers select for each:

  - The maze module id. This should be selected before the other settings can be changed.

  - AM448 device connection to CHA (By clicking the Change… button)

  - Am448 device connection to CHB (By clicking the Change… button)

  - Amplifier channel B backup or normal usage.

  - Charger Group: When multiple amplifiers have the same charger group, they should work together to charge 1 set of batteries.

### BGM Tab:

- Select which audio inputs are enabled.

- Select if the input is used for live evacuation events.

- When the impact has a maze module available, the BGM input can also be selected to be used as an audio input for the maze network.

- Set the equalizer options. (See 3.1.14.1)

- Set the volume for the audio input channel. (Default: -9 dB or 0dB, depending on the “Default Audio Level” setting)

Image 9 Impact Background Music Tab

### Evac Inputs Tab:

- Select if the input is monitored. When monitoring is disabled, faults will not be reported.

- Select if the input is normally open or normally closed. (Default: Normally Open)

- Select if the input is pulse triggered. When this option is enabled the event will stay active until the device is reset. Otherwise it will be set to level sensitive. (Default: Level sensitive)

- Select the input function. This makes it possible to use the input for different types of event activation or system functions. (Default: Event Activation (Level))

- Select which events are activated by the input.

Image 10 Impact Evac Inputs Tab

### GPO Tab:

- Select when the output is activated. (Default: Active High)

  - Active High: The output is closed when a connected event is active.

  - Active Low: The output is closed when a connected event is inactive.

- Select if the output is used as a system reset output. This means that, after a system reboot, the output will be activated. The duration that the output will be active can be specified in the global system settings. (See 3.7.1)

- Select what zone state and / or device fault activates the output. (See 3.1.14.2)

- Show the event names that trigger this output.

Image 11 Impact GPO Tab

### More Tab:

- Select the monitoring tone level. (Default: -35 dB)

- Select if a high level 20 kHz tone is activated during emergency audio types (All evacuation and alert types)

- Select if a high level 20 kHz tone is activated during paging audio types (All general types, except BGM)

- Select the high level 20 kHz tone level. (Default: -25 dB)

Image 12 Impact More Tab

### Edit Device Dialog Expander

This dialog is used to edit an expander device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

### Edit Device Dialog Commercial Microphone Pushbutton (CMP)

This dialog is used to edit a CMP device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The CMP device has the following 2 tabs with settings:

### Zones Tab:

- Select which zone is connected to each selection button. A zone can only be linked to 1 button at a time.

- When checking the ‘Select First Available Zones’ box, it will connect the first 6 zones to the buttons.

Image 13 CMP Zones Tab

### More Tab:

- Select the ‘Talk Button Mode’. ‘Push To Talk’ or ‘Toggle To Talk’ can be selected. (Default: Push to talk)

- Select the ‘Chime Mode’ that is used. (Default: No chime)

- Select the ‘Microphone Gain’. ((Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select if the exclusive zone selection is used. This restricts the zone selection, so always 1 zone is selected. (Default: false)

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

Image 14 CMP More Tab

### Edit Device Dialog Fireman Microphone (FM)

This dialog is used to edit a FM device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The FM device has the following 2 tabs with settings:

### Zones Tab:

- Select which zones are activated by the microphone.

Image 15 FM Zones Tab

### More Tab:

- Select the ‘Microphone Gain’. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

Image 16 FM More Tab

### Edit Device Dialog GPIO (GPIO)

This dialog is used to edit a GPIO device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The GPIO device has the following 4 tabs with settings:

### Inputs Tab:

- Select if the input is monitored. When monitoring is disabled faults will not be reported.

- Select if the input is normally open or normally closed. (Default: Normally Open)

- Select if the input is pulse triggered. When this option is enabled the event will stay active until the device is reset. Otherwise it will be set to level sensitive. (Default: Level sensitive)

- Select the input function. This makes it possible to use the input as: silence input, reset input, mute buzzer input, external front panel related functions or event activation. (Default: Event Activation (Level))

Image 17 GPIO Inputs Tab

### Outputs Tab:

- Select when the output is activated. (Default: Active High)

  - Active High: The output is closed when a connected event is active.

  - Active Low: The output is closed when a connected event is inactive.

- Select the output function. This makes it possible to use the input as: system reset output, external buzzer output, zone selection output or GPO activation. (Default: GPO)

  - In the GPO ’Function’ dropdown menu: Select what zone state and / or device fault activates the output. (See 3.1.14.2)

  - On system reset function: Select if the output is used as a system reset output. This means that, after a system reboot, the output will be activated. The duration that the output will be active can be specified in the global system settings. (See 3.7.1)

  - On external buzzer function: The output will be active while the buzzer is active in the system. (When a GPIO group is used, the external buzzer function should be connected to the same GPIO that also activates the live audio signals, which means the line and microphone inputs).

  - On zone selection function: Select a zone connected to the input of this GPIO. When it is selected, the output will activate.

Image 18 GPIO Outputs Tab

### Audio In Tab:

There are 2 groups of settings available in this tab. The settings for the ‘Line Input’ and the settings for the ‘Microphone Input’.

Note: The ‘Line Input’ settings are only visible if it’s not used by the selected protocol in the ‘More’ tab.

### Line Input:

- Select if the ‘Line Input’ is enabled. (Default: Disabled)

- Select if the ‘Line Input’ is monitored. When enabled, it reports a fault if there is nothing connected. (Default: Disabled)

- Select if the ‘Line Input’ is used as a live evac input. Otherwise it will be seen as a BGM input. This setting makes the input available in the live evac event or the BGM event creation. (Default: Disabled).

- Select the ‘Line Input’ audio gain. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

### Mic Input:

- Select if the ‘Microphone Input’ is enabled. (Default: Disabled)

- Select if the ‘Microphone Input’ audio gain. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select the zones that are activated by the microphone.

Image 19 GPIO Audio In Tab

### More Tab:

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

- Select the chime that is used. (Default: No chime)

- Select the connected group ID. All GPIO devices with the same group id (on the same master), will work together to make it possible to create a bigger external panel. This allows, for example, paging from one GPIO to use zone selection from another GPIO in the group (Default: None)

- Select the serial protocol that is used. Currently only the control station protocol is supported. (Default: None)

The control station protocol has the following settings:

- Select if the audio monitoring is enabled. When enabled it reports a fault if there is nothing connected to the line input. (Default: Disabled)

- Select if the data link is monitored. (Default: Disabled)

- Select the line input gain. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

Image 20 GPIO More Tab

### Edit Device Dialog Fireman and Gooseneck Microphone Touchscreen Console (FMTC)

This dialog is used to edit a FMTC device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The FMTC device has the following 7 tabs with settings:

### General Zones Tab:

- Select which zones and/or zone groups are available for general paging

Image 21 FMTC General Zones Tab

### Evac Zones Tab:

- Select which zones and/or zone groups are available for evac paging.

Image 22 FMTC Evac Zones Tab

### Evac Sources Tab:

- Select which evac or alert audio messages can be activated.

### General Sources Tab:

- Select which general audio messages and BGM inputs can be activated.

Image 23 FMTC Sources Tab

### Actions Tab:

- Select which events are available. (Default: Silence buzzer, system reboot and lamp test are always selected)

Image 24 FMTC Actions Tab

### Volume Tab:

- Select what volume events can be activated.

Image 25 FMTC Volume Tab

### More Tab:

- Select the language of the touchscreen (Default: English)

- Select the ‘Talk Button Mode’. ‘Push To Talk’ or ‘Toggle To Talk’ can be selected. (Default: ‘Push To Talk’)

- Select the ‘Chime Mode’ that is used. (Default: No chime)

- Select the gooseneck ‘Microphone Gain’. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select the ‘Fireman Microphone Gain’. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select if there is ‘Buzzer Feedback On User Action’ (Default: Disabled)

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

- Select if ‘Pin Code Enabled’ is checked. The pin code is always 4 digits

Image 26 FMTC More Tab

### Edit Device Dialog Fireman Microphone Touchscreen Console (FMT)

This dialog is used to edit a FMT device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The FMT device has the following 3 tabs with settings:

### Evac Zones Tab:

- Select which zones and/or zone groups are available for evac paging.

Image 27 FMT Zones Tab

### Evac Sources Tab:

- Select which audio messages can be activated. Only evacuation and alert messages can be selected here.

Image 28 FMT Sources Tab

### More Tab:

- Select the ‘Language’ of the touchscreen (Default: English)

- Select the ‘Fireman Microphone Gain’. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select if there is ‘Buzzer Feedback On User Action’ (Default: Disabled)

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

Image 29 FMT More Tab

### Edit Device Dialog Gooseneck Microphone Touchscreen Console (CMT)

This dialog is used to edit a CMT device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The CMT device has the following 5 tabs with settings:

### General Zones Tab:

- Select which zones and/or zone groups are available for general paging.

Image 30 CMT Zones Tab

### General Sources Tab:

- Select which audio messages can be activated. Only general messages and BGM inputs can be selected here.

Image 31 CMT Sources Tab

### Actions Tab:

- Select which events are available.

Image 32 CMT Actions Tab

### Volume Tab:

- Select what volume events can be activated.

### More Tab:

- Select the ‘Language’ of the touchscreen (Default: English)

- Select the ‘Talk Button Mode’. Push To Talk’ or ‘Toggle To Talk’ can be selected. (Default: Push to talk)

- Select the ‘Chime Mode’ that is used. (Default: No chime)

- Select the gooseneck ‘Microphone Gain’. (Default: -9 dB or 0 dB, depending on the “Default Audio Level” setting)

- Select if there is ‘Buzzer Feedback On User Action’ (Default: Disabled)

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: false)

- Select if ‘Pin Code Enabled’ is checked. The pin code is always 4 digits

Image 33 CMT More Tab

### Edit Device Dialog Switching Unit (SW6)

This dialog is used to edit a SW6 device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Change the output monitoring. (Completely on or completely off)

- Select the class A wiring mode (all outputs will be coupled as pairs, since a loop is expected on the output)

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The SW6 device has the following 3 tabs with settings:

### Outputs Tab:

- Select if the output lines are enabled. (Default: enabled)

- Select if the output lines ‘EOL Monitoring’ is checked. Disable when line faults should not be reported. (Default: enabled)

- Select if the ‘Disable Short Detection ‘is checked. (This can only be changed when the EOL monitoring is disabled) (Default: disabled)

- Select the ‘Impedance Tolerance’. (Default: 50%)

Image 34 SW6 Outputs Tab

### Inputs Tab (With C500):

- Select if input is enabled. (Default: enabled)

- Select if input is monitored. (Default: enabled)

Image 35 SW6 Inputs Tab (with C500)

### Inputs Tab (With Impact):

- Select if the input is enabled. (Default: enabled)

- Select if the input is monitored. (Default: enabled)

- Select if input B is used as a backup group. (This option is only available when 0 amplifiers are configured for the impact device. Otherwise these settings are selected in the impact amplifier tab See 3.1.3.1.)

Image 36 SW6 Inputs Tab (with impact)

### More Tab:

Select if the redundant link is used. This means that both local net ports should be connected. (Default: false)

Image 37 SW6 More Tab

### Edit Device Dialog AM448 Unit (AM448)

This dialog is used to edit a AM448 device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The AM448 device has the following 3 tabs with settings:

### Outputs Tab:

- Select if the output lines are enabled. (Default: enabled)

- Select if the output lines ‘EOL Monitoring’ is checked. Disable when line faults should not be reported. (Default: enabled)

- Select the ‘Impedance Tolerance’. (Default: 50%)

Image 38 AM448 Outputs Tab

### Inputs Tab:

- Select if input is enabled. (Default: enabled)

- Select if input is monitored. (Default: enabled)

Image 39 Am448 Inputs Tab

### More Tab:

Select if the redundant link is used. This means that both local net ports should be connected. (Default: false)

Image 40 Am448 More Tab

### Edit Device Dialog Fireman Microphone Wall Bracket (FMWB)

This dialog is used to edit a FMWB device and has the following general options:

- Change the device name.

- Change the device ID.

- Change the device priority. A lower number indicates a higher priority.

- Select if the integrated ‘Fireman Microphone’ is available. (Default: disabled)

- Restore the default settings. This will load the default settings for either the current tab or for all tabs. This depends on the radio button selection.

- Save the changes by pressing the ‘Ok’ button or select the next device from the dropdown list.

The FMWB device has the following 2 tabs with settings:

### Zones Tab:

- Select which zone is connected to each selection button. A zone can only be linked to 1 button at a time.

- When checking ‘Select First Available Zones’ it will connect the first 6 zones to the buttons.

Image 41 FMWB Zones Tab

### More Tab:

- Select if the ‘Redundant Link’ is used. This means that both local net ports should be connected. (Default: False)

- Select the ‘Microphone Gain’. (Default: -9dB or 0 dB, depending on the “Default Audio Level” setting)

Image 42 FMWB More Tab

### Additional Dialogs

The following dialogs are used in multiple places in the application:

### Equalizer Dialog

This dialog is used to setup the equalizer settings.

- Select the ‘Gain’ for the filter. (Default: 0 dB)

- Select the ‘Frequency’ of the filter. (Default: 20 Hz)

- Select the ‘Q’ factor. (Default: 0,10)

- Select the filter ‘Type’. (Default: Low Shelving for filter 1, High Shelving for filter 5 and Peak for all remaining filters.

The following filter types are available:

- Allpass Filter

- Bandpass Filter

- Peak Filter

- Notch Filter

- Lowpass Filter

- Highpass Filter

- Low Shelving Filter

- High Shelving Filter

Note: The first filter setting is hardcoded on the C500 BGM input when the IFM is connected.

Image 43 Equalizer Dialog

### GPO Output Connections Dialog:

This dialog is used to setup the zone state and device fault connection to a GPO.

- Select the zone that should be checked for the ‘Zone State’.

- Select the zone states in the select zone that should activate the GPO.

- Select the device(s) that activate the GPO in case of a device fault.

Image 44 GPO Output Connection Dialog

## Zone overview

The zone overview contains the following buttons:

- ‘Add’ button: Opens a dialog to create a new zone or zone group. (When holding the Ctrl button, it gives the option to add a zone per unused speaker line)

- ‘Edit’ button: Opens a dialog to edit the selected zone or zone group.

- ‘Delete’ button: Remove the selected zone(s) and zone group(s). (When holding the Ctrl button, it gives the option to delete all zones)

Image 45 Zones Overview

### Add Zone Dialog

This dialog is used to create a new zone or zone group and has the following options:

- Give the zone a name. If this field is left empty, a name is automatically generated.

- Select the zone type. Select the zone or zone group type.

### Add Zone

- Select the speaker lines that are included in the zone.

- Select the zone id.

- Select if the zone is excluded from zone group indication.

- Create the zone by pressing the ‘Ok’ button.

Each table cell can have the following states:

- Checkbox: The speaker line is available.

- Dash (-): The speaker line is already used in another zone.

- Empty: The speaker line does not exist. This typically happens for bridged amplifiers.

The ‘Ok’ button is greyed out when no speaker line is selected, since a zone cannot be created without a single speaker line.

Image 46 Add Zone Dialog

### Add Zone Group

- Select the zones that are included in the zone group.

- Select the zone group id.

- Create the zone group by pressing the ‘Ok’ button.

The ‘Ok’ button is greyed out when no zones are selected, since a zone group cannot be created without a zone.

Image 47 Add Zone Group

### Edit Zone Dialog

This dialog is used to edit an existing zone or zone group and has the following option:

- Change the zone name.

### Edit Zone

- Change the speaker lines that are included in the zone.

- Change the zone id.

- Change if the zone is excluded from zone group indication

- Save the changes by pressing the ‘Ok’ button or select the next zone or zone group from the dropdown list.

Each table cell can have the following states:

- Checkbox: The speaker line is available.

- Dash (-): The speaker line is already used in another zone.

- Empty: The speaker line does not exist. This typically happens for bridged amplifiers.

When the user changes a result in a zone without speaker lines, they get prompted to remove this zone or going back and edit it. This happens because a zone cannot exist without any speaker lines.

Image 48 Edit Zone Dialog

### Edit Zone Group

- Change the zones that are included in the zone group.

- Change the zone group id.

- Save the changes by pressing the ‘Ok’ button or select the next zone or zone group from the dropdown list.

When the user changes a result in a zone group without zones, they get prompted to remove this zone group or going back and edit it. This happens because a zone group cannot exist without any zones.

Image 49 Edit Zone Group

## Sources overview

The sources tab contains settings for the message configuration and the selection of user defined names for the enabled analog inputs. When maze devices are configured, the maze audio channel can also be given a name.

For message file selection the following buttons are used:

- ‘Add’ button: Opens a file chooser to select new audio files.

- ‘Delete’ button: Removes the selected audio files. (When holding the Ctrl button, it gives the option to delete all messages)

Note: The messages should have the following format: PCM, 16 bits, mono, 24 kHz and be less than 60 seconds in length. From version 5.3 mp3 and wav files can be converted to this format by the application.

After successfully adding audio files the following options are available:

- Type: Assign a message type to the audio file. (Evac, Alert or general purpose)

- Volume: Select the volume of the message. (Default: 0 dB)

- User Defined Name: This name will be used in the application and on the TSC, instead of the default type name.

- Change File: This opens a file selection to change the audio file that is linked to this type.

- Play Message: Play the selected audio file over the computer speakers as reference. The volume setting is not applied during this playback.

Image 50 Sources Overview

Supported Message:

- Evac Message (1 x)

- Alert Message (2 x)

- General Message (13 x)

- Chime Message (2 x)

Analog Input Names:

Up to 64 analog inputs can be configured with a user defined name. When maze devices are configured, the maze audio channel can also be given a name. This name will then also be used for buttons and zone states on the touchscreen devices.

Maze Audio Channels:

For each maze module that is used in the system, the module id and the maze audio channels should be known in the configuration. All devices with a maze module selected in the configuration will automatically show up. Then the user should select which audio channels are used by this module. This can either be entered manually or done via the “Import Maze Settings” button. Clicking this button will ask you for a settings file generated by the Maze Manager software.

## Event overview

The event overview contains the following buttons:

- ‘Add’ button: Opens a dialog to create a new event.

- ‘Edit’ button: Opens a dialog to edit the selected event.

- ‘Delete’ button: Remove the selected event(s). (When holding the Ctrl button, it gives the option to delete all events)

Image 51 Events Overview

### Add Event Dialog

This dialog is used to create a new event and has the following general options:

- Give the event a name. If this field is left empty a name is automatically generated.

- Select the event type.

- Select the event id.

- Create the event by pressing the ‘Ok’ button.

The following nine event types can be created:

### Amplifier Volume Event

- Select the default volume that is used after a system reboot. (Default: 0 dB)

- Select the ‘Headroom’. This selects how much the user can increase the volume above the default volume. (Default: 0dB)

- Select which amplifiers are updated with this event. (A maximum of 64 amplifiers can be selected per event and each amplifier can only be selected in 1 volume event)

Image 52 Amplifier Volume Event

### Background Music Event

- Select the audio input that is used. This is selected from a list of all available inputs.

- Select in which zones the background music is activated.

- Select the GPO’s that are activated.

Image 53 Add Background Music Event

### External Fault Event

- Select if a zone fault should be triggered. Otherwise only a general fault will be generated by this event.

Image 54 Add External Fault Event

### GPO Event

- Select the GPO’s that are activated.

Image 55 Add Gpo Event

### Line Input Volume Event

- Select the ‘Default Volume’ that is used after a system reboot. (Default: 0 dB)

- Select the ‘Headroom’. This selects how much the user can increase the volume above the default volume. (Default: 0dB)

- Select which ‘Line Input’ is updated with this event. (Each line input can only be selected in 1 volume event)

Image 56 Line Input Volume Event

### Live Evacuation Event

- Select the audio input that is used. This is selected from a list of all available inputs.

- Select in which zones the live evacuation is activated.

- Select the GPO’s that are activated.

Image 57 Add Live Evacuation Event

### Maze Bgm Event

- Select the maze audio channel that is used. This is selected from a list of all available audio channels.

- Select in which zones the maze BGM is activated. Only zones that exclusively have maze amplifiers as outputs can be selected.

- Select the GPO’s that are activated.

Image 58 Add Maze Bgm Event

### Message Event

- Select the message type that is activated. Choose from General 1 – General 17.

- Select the number of repetitions. (Default: Continuous Playback is selected)

- Select in which zones the message is activated.

- Select the GPO’s that are activated.

Image 59 Add Message Event

### Phased Evacuation Event

- Select per zone the message type that is activated. Choose from ‘Evac’, ‘Alert1’ and ‘Alert2’ types.

- Select the GPO’s that are activated.

Image 60 Add Phased Evacuation Event

### Edit Event Dialog

This dialog is used to edit events and has the following general options:

- Change the event ‘Name’.

- Change the event ‘id’.

- Save the changes by pressing the ‘Ok’ button or select the next event from the dropdown list.

The following nine event types can be edited:

### Amplifier Volume Event

- Select the ‘Default Volume’ that is used after a system reboot. (Default: 0 dB)

- Select the ‘Headroom’. This selects how much the user can increase the volume above the default volume. (Default: 0dB)

- Select which amplifiers are updated with this event. (A Maximum of 64 amplifiers can be selected per event and each amplifier can only be selected in 1 volume event)

Image 61 Edit Amplifier Volume Event

### Background Music Event

- Change the ‘Select BGM input’ that is used. This is selected from a list of all available inputs.

- Change in which zones the background music is activated.

- Changes the GPO’s that are activated.

Image 62 Edit Background Music Event

### External Fault Event

- Change if a zone fault should be triggered. Otherwise only a general fault will be generated by this event.

Image 63 Edit External Fault Event

### GPO Event

- Change the GPO’s that are activated.

Image 64 Edit Gpo Event

### Line Input Volume Event

- Select the ‘Default Volume’ that is used after a system reboot. (Default: 0 dB)

- Select the ‘Headroom’. This selects how much the user can increase the volume above the default volume. (Default: 0dB)

- Select which ‘Line Input’ is updated with this event. (Each line input can only be selected in 1 volume event)

Image 65 Edit Line Input Volume Event

### Live Evacuation Event

- Change the audio input that is used. This is selected from a list of all available inputs.

- Change in which zones the live evacuation is activated.

- Change the GPO’s that are activated.

Image 66 Edit Live Evacuation Event

### Maze Bgm Event

- Change the maze audio channel that is used. This is selected from a list of all available audio channels.

- Change in which zones the maze BGM is activated.

- Change the GPO’s that are activated.

Image 67 Edit Maze Bgm Event

### Message Event

- Change the message type that is activated. Choose from General 1 – General 13.

- Change the number of repetitions.

- Change in which zones the message is activated.

- Change the GPO’s that are activated

Image 68 Edit Message Event

### Phased Evacuation Event

- Change the message type that is activated per zone. Choose from ‘Evac’, ‘Alert 1’ and ‘Alert 2’ types.

- Change the GPO’s that are activated.

Image 69 Edit Phased Evacuation Event

## Evac Matrix

The event matrix shows what message types are used when an evacuation input is activated. Each column contains the device id and the evacuation input that is activated.

Each table cell can have the following states:

- Evac type: The evacuation message is activated. The background color is red.

- Alert 1 type: The alert1 message is activated. The background color is orange.

- Alert 2 type: The alert2 message is activated. The background color is orange.

- Dash (-): The zone is not used by any message.

Note: This is a read-only table that displays the result of the device and event settings related to the evac message event.

Image 70 Evac Matrix

## Live Monitoring

Starting from version 5.1, this application supports reading of all device faults and log files from any connected global net device. To start live monitoring, the user should be connected to the system and the live monitoring tab should be opened.

Image 71 Live Monitoring Tab

### Device Faults and Live Device Data

Pressing the ‘Refresh Device List’ button will initiate a scan for all connected devices. These will be continuously polled for fault information. When a device supports live monitoring of data the ‘Live Monitoring’ button will be enabled. When the ‘Delete Log File’ is pressed the log files on the SD-Cards will be cleared and the system will reboot.

By clicking the ‘Live Monitoring’ button one of the dialogs below will be shown.

### C500 Live Monitoring Dialog

The C500 live monitoring dialog shows impedance, temperature and fault information for each amplifier. It also shows information related to the charger, when this is connected. It also retrieves the stored impedance values when opened and these can later be updated by pressing the “Get Reference Impedance” button.

Image 72 C500 Live Monitoring

### Impact Live Monitoring Dialog

The Impact live monitoring dialog shows the following data:

- The expected amplifier firmware version from the impact device.

- Per amplifier it shows:

  - The amplifier version.

  - Any active fault information.

  - The battery impedance. (Only when it has a temperature sensor)

  - The battery voltage in V. (Only when it has a temperature sensor)

  - The battery temperature in °C. (Only when it has a temperature sensor)

  - The current charging status.

  - The charging current in mA.

Image 73 Impact Live Monitoring

### SW6 Live Monitoring Dialog

The SW6 live monitoring dialog shows the following data:

- The input voltage for input A and B.

- The currently measured impedance for each speaker line.

- The reference impedance. This is the impedance that was saved during calibration.

- The deviation from the reference impedance.

Image 74 SW6 Live monitoring

### AM448 Live Monitoring Dialog

The Am448 live monitoring dialog shows the following data:

- The input voltage for all inputs

- The currently measured impedance for each speaker line.

- The reference impedance. This is the impedance that was saved during calibration.

- The deviation from the reference impedance.

Image 75 AM448 Live monitoring

### Log File

Pressing the ‘Get Log File’ button will initiate a scan for all connected devices. Followed by the option to select the global net device where the log file should be downloaded from. Once downloaded it will show all entries in the text field.

Note: For correct timestamps, the real time clock should be synchronized by pressing the ‘Set Date Time’ button in the More tab.

Image 76 Log File

To track down certain types of faults more efficiently, some filters can be selected.

Image 77 Log File Filters

- Selecting the ‘Device Id’ will filter all data related to the selected device

- Selecting the ‘Device Type’, will filter all data related to the device type

  - Once a ‘Device Type’ is selected, a specific fault related to that type can also be used.

- Selecting the ‘Start Date’ and ‘End Date’ of the entries. (As long as the start and end date are the same, the complete range is used.

## More Settings

## Global Configuration Settings

- Multi-Channel Streaming: This selects if multiple microphones, BGM or live evac audio streams can be active in the system at the same time. (Default: disabled)

  - Zone Collision: This indicates if an audio stream will activate when the selected zones are partially in use. Accepted means it will activate and rejected means it will not. (This option is only available when Multi Channel Streaming is enabled)

- Reset Relay Pulse Length: This value selects the pulse length of the reset relay. This is used by C500 and GPIO devices. (Default: 1000ms)

- Zone Selection Timeout: This value selects the number of seconds it takes before zone selection is cleared. When set to 0, this feature is disabled. (Default: 0s)

- Amplifier Power Save Mode: When checked, the amplifiers are using a power save mode when idle. This can cause an audible tick every ~30 seconds. (Default: disabled)

- Global Net Monitoring: When checked, the system monitors the global net ports and handles and reports errors. Otherwise global net faults are ignored. (Default: disabled)

- Keep General Fault State Until Reset: When checked, the system will keep the fault state active even when the fault condition is gone again. Otherwise fault state can be deactivated when the fault condition is restored. (Default: disabled)

- Report Fault On Decalibrated Speaker Lines: When checked, the sw6 will generate a fault if the speaker lines are not calibrated.

- Power Supply Surveillance: When checked, the C500 devices monitor and report power supply faults. Otherwise these faults are ignored. (Default: enabled)

  - Allow Commercial Activity On Mains Fault: This allows the usage of commercial messages and paging while a mains fault is detected.

## Application Settings

- Language: The language of the application.

- COM Port: The com port that is used by the online configuration.

- Default Audio Level 0 dB: Select the default amplifier volume, the analog inputs volume and the microphone gain to 0 dB by default instead of the -6 dB or -9 dB it normally uses.

- Show Download Device Selection: When checked, a device selection dialog will be shown when more than 1 device is detected during configuration downloading. Otherwise the first available device is selected.

- Mute Buzzer On Fault (When Connected To The System): When the manager application is connected to the system, it will send mute buzzer commands. This should help to keep the buzzer off while configuring the system.

- Use Preferred Device Ids: When creating devices, select the device id that is normally used for the selected type. (So A0 for CMP, B0 for FM, etc.)

- Enable Pin Code For Configuration: When checked, the user should select a pin code. This pin code should be entered again, before uploading of downloading on configuration settings. The application will automatically try to use the last set pin code to connect.

- Enable Password For This Program: When checked, the user should select a password for the application, this password is requested during start-up of the manager software. Only after selecting the correct password will the application be usable.

## Synchronize Time

- Set Date Time Button: This will synchronize the local time on the computer with the real time clocks in the system. This should be done when connected to the system, so the log file has correct timestamps.

Image 78 More Tab

## Clear, Open, Save, Download and Upload configuration

This chapter describes the clear, open, save, download and upload configuration options.

Image 79 Clear, Open, Save, Download and Upload Buttons

### Clear Configuration

The current configuration settings can be removed at any time by using the ‘Clear Configuration’ button. This removes all data and returns the application to the initial start-up state.

### Open Configuration

Saved configuration files can be loaded by using the ‘Open’ button. This opens a file chooser dialog where the user has to select a .4Evac file.

### Save Configuration

The current configuration can be saved by using the ‘Save’ button. This opens a directory chooser dialog where the user has to select a folder. When selecting a SD-card that will be inserted in a device, the root folder should be selected.

To save the current configuration, the following requirement should be met:

- At least 1 device is created.

- Evac message type is assigned to an audio file.

Two different file types are created when the save is successful.

- .dat files: This contains the binary data that the devices use.

- .crc files: This contains the .dat file checksum and is used to confirm the data integrity.

### Read Configuration

Existing configuration files can be retrieved from the system via the online configuration mode. Pressing this button will start the configuration file download. (See section 1.2 for more information about the online configuration)

### Send Configuration

The current configuration files can be send to the system via the online configuration mode. Pressing this button will start the configuration file upload. (See section 1.2 for more information about the online configuration)

# Supported devices

The table below shows the device(s) that can be configured with the 4Evac Manager software.

| Device Name | Picture | Technical Specification |
| --- | --- | --- |
| Compact 500 (C500) |  | http://www.4evac.com/technical-specifications |
| Impact |  | https://www.4evac.com/impact-multi-channel-vacie-system |
| Expander |  | https://www.4evac.com/impact-controller-expander |
| Commercial Microphone Pushbutton (CMP) |  | https://www.4evac.com/fireman-microphones |
| Fireman Microphone (FM) |  | https://www.4evac.com/fireman-microphones |
| Gpio Device (GPIO) |  |  |
| ##### Fireman and gooseneck microphone Console (FMTC) |  | https://www.4evac.com/fireman-microphones |
| ##### Fireman microphone touchscreen Console ##### (FMT) |  | https://www.4evac.com/fireman-microphones |
| ##### Gooseneck Microphone Console (CMT) |  | https://www.4evac.com/fireman-microphones |
| ##### Switching Unit (SW6) |  | https://www.4evac.com/sw6-switching-module |
| ##### Amplifier Monitoring Unit (AM448) |  |  |
| ##### Fireman Microphone Wall Bracket ##### (FMWB) |  | https://www.4evac.com/fireman-microphones |

The amplifier hardware should always be checked for the correct configuration. This means the jumpers position and the loudspeakers connection is verified. (see the installation manual for more information)

A normally open input is activated by closing a switch connected to this input.
  A normally closed input is activated by opening a switch connected to this input.

A normally open input is activated by closing a switch connected to this input.
  A normally closed input is activated by opening a switch connected to this input.

A normally open input is activated by closing a switch connected to this input.
  A normally closed input is activated by opening a switch connected to this input.